## Slide 1: Frequency Response and Control in Power Systems
Megan Swanson
SUPERB Project
July 2017

## Slide 2: Overview
Purpose
Frequency Response and Control in Power Systems
Modeling
Impact of variable renewable energy
Proposed methods

## Slide 3: Purpose
The purpose of this review is to increase my understanding of frequency response and control in power systems with a focus on how variable renewable energy affects the system.

## Slide 4: Frequency Response and Control in Power Systems
Inertia
  Lower inertia = faster frequency response
Damping
  Lower damping = faster frequency response
Faster frequency response = more severe consequences
Notes: Frequency Response is how the system responds after a significant loss of generation.
Frequency control in power systems is made possible because of the rotational inertia from conventional generators in the system. This inertia is what keeps the system frequency from deviating too much when generation losses occur because the inertia from the generators keep spinning at the same rate for a set time and the PFR is able to kick in before it changes too much. Without this inertia, or with decreased inertia, the system frequency will change much faster, often too quickly for the PFR to to kick in before it drops below the safe values which can cause a cascade of trips and interrupt service.

## Slide 5: Modeling
Simulation software
  Complicated (many variables)
  Expensive (time and money)
Full network models
  Complicated (many variables)
  Time
Simplified Models (Aggregated Swing eq. Average Freq.)
  Marginally less accurate
  Easy to use
Notes: In power systems, the frequency response can be modeled with equations or simulation software. Simulations offer very precise results, however, they require knowledge of many different parameters related to all components of a system and are therefore difficult to use for large systems. Similarly, full network models have a similar restraint in which many parameters are necessary to be concise and they become very difficult to manage for large systems. Therefore, researchers tend to use simplified models to examine larger systems because they can be adapted to take less variables and still produce a relatively accurate result.

## Slide 6: Swing Equation
Notes: We are going to use the swing equation to model the frequency response because it is more accurate than…
We are using the aggregated swing equation to adapt the equation to model a whole network.

## Slide 7: Impact of Renewables
No inertia (H = 0)
Increased frequency response
Less control
Notes: Variable renewable energy sources like wind and solar do not contribute any rotational inertia. Because of this, when more renewables are incorporated into power systems, the overall system inertia decreases. A decrease in inertia means that the frequency response in the event of a major fault or loss of generation (basically any major power imbalance) will be much more severe because the entire system will react faster when there is less inertia to maintain the frequency. This response will be too quick for the primary frequency response controls and could cause cascading trips and wide spread blackouts.

## Slide 8: Proposed Methods
Synthetic or Virtual Inertia
Energy Storage Systems

## Slide 9: Virtual Inertia
WTGs
Pros:
Cons:

## Slide 10: Energy Storage Systems
Pros:
Cons: